- Section 224213 
Commercial Water Closets and Urinals - Zurn

PART 1  GENERAL

Section Includes

Flush valve water closets.

Urinals.

Flush valves for water closets.

Flush valves for urinals.

Fixture carriers.

Related Requirements

Section ​<< 221005 - Plumbing Piping>>​.

Reference Standards

ADA Standards - 2010 ADA Standards for Accessible Design; 2010.

ASME A112.6.1M - Floor-Affixed Supports for Off-the-Floor Plumbing Fixtures for Public Use; 1997 (Reaffirmed 2017).

ASME A112.19.2 - Ceramic Plumbing Fixtures; 2024.

ASSE 1037/ASME A112.1037/CSA B125.37 - Performance Requirements for Pressurized Flushing Devices for Plumbing Fixtures; 2020.

ICC A117.1 - Accessible and Usable Buildings and Facilities; 2017.

Submittals

See Section ​<< 013000 - Administrative Requirements>>​ for submittal procedures.

Product Data:  Provide manufacturer's literature and data sheets for each product. Include information on fabrication materials, dimensions, rough-in requirements, finishes, and installed accessories.

Sustainable Design Documentation:  Submit appropriate evidence that products comply with specified requirements.

Operation and Maintenance Data:  Provide for flush valves. Include exploded view and replacement parts lists.

Specimen warranty.

Executed warranty.

Software:  Provide QR codes and access to plumbSMART software and mobile application required in this section; provide associated registration documentation and support contact information. Indicate registration is in <<Owner>>'s name.

Mobile Applications:  Provide QR codes and access to plumbPRO mobile application required in this section, provide associated registration documentation and support contact information. Indicate registration is in ​​<<Owner>>​​'s name.

Maintenance Materials:  Furnish the following for ​​​<<Owner>>​​​'s use in project maintenance:

See Section ​<< 016000 - Product Requirements>>​ for additional provisions.

Flush Valve Diaphragm Replacement Kit:  << One;  Two; or  ______>> for each type and size.

Waterless Urinal Trap-Sealing Liquid:  << 1 gal (3.8 L);  2 gal (7.6 L); or  _____ gal (_____ L)>> for every << five;  ten; or  ___>> waterless urinals on project.

Delivery, Storage, and Handling

See Section ​<< 017419 - Construction Waste Management and Disposal>>​ for packaging waste requirements.

Receive, inspect, handle, and store products in accordance with manufacturer's instructions.

Keep products in original manufacturer's packaging and protect from damage until ready for installation.

Store vitreous china fixtures indoors or in weathertight enclosure. Protect from weather and dirt. Elevate above grade. Do not allow fixtures to accumulate water. Do not allow to freeze.

Store flush valves indoors or in weathertight enclosure. Protect from water and dirt. Elevate above floor.

Warranty

See Section ​<< 017800 - Closeout Submittals>>​ for additional warranty requirements.

Manufacturer Warranty:  Provide manufacturer's warranty for the following products from date of purchase. Complete forms in <<Owner>>'s name and register with manufacturer.

Water Closets:  3 years.

Urinals:  3 years.

Flush Valves:  3 years.

PART 2  PRODUCTS

Manufacturers

Basis of Design:  Zurn Water, LLC:  www.zurn.com/#sle.

Other Acceptable Manufacturers:

​<< ____>>​.

​<< ____>>​.

Substitutions:  ​<< See Section 016000 - Product Requirements; or  Not permitted>>​.

Source Limitations:  Furnish products<< , accessories, and appurtenances;    ______; or  None - N/A>> by single manufacturer<<  and obtained from single supplier;    ______; or  None - N/A>>.

General Requirements

Minimum Fixture Supply Pressure:  ​​<< 25 psi (172 kPa); or  _____ psi (_____ kPa)>>​​ unless stated otherwise.

Maximum Fixture Supply Pressure:  ​​<< 80 psi (552 kPa); or  _____ psi (_____ kPa)>>​​ unless stated otherwise.

ADA:  Where indicated as ADA-compliant, provide fixtures complying with <<ADA Standards>> and <<ICC A117.1>>.

WaterSense:  Provide products labeled as complying with EPA WaterSense.

Flush Valve Water Closets

Wall-Mounted, Back-Outlet, Flush Valve Water Closets​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​:

Basis of Design:  Zurn Water, LLC; Z5615-BWL.

Description:  <<ASME A112.19.2>>, vitreous china, siphon-jet flush.

Provide with ZurnSHIELD glaze to inhibit growth of mold, mildew, and bacteria.

Bowl:  Elongated.

Spud:  Top spud, << 1-1/2 inches (38 mm)>>.

Color:  White.

Toilet Seat:  Provide ​<< as indicated on drawings;  manufacturer's white, elongated, open front seat, less cover, with stainless steel check hinges; or  ___>>​​.

Floor-Mounted, Bottom-Outlet, Flush Valve Water Closets​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​:

Basis of Design:  Zurn Water, LLC; Z5654-BWL1, << 14-inch (356 mm)>>​ rim height.

Basis of Design:  Zurn Water, LLC; Z5655-BWL1, << 15-inch (381 mm)>> rim height.

Basis of Design:  Zurn Water, LLC; Z5665-BWL1, << 16-3/4-inch (425 mm)>> ADA rim height.

Description:  <<ASME A112.19.2>>, vitreous china, siphon-jet flush. Provide bolt caps.

Provide with ZurnSHIELD glaze to inhibit growth of mold, mildew, and bacteria.

Bowl:  Elongated.

Spud:  Top spud, << 1-1/2 inches (38 mm)>>.

Color:  White.

Toilet Seat:  Provide ​​<< as indicated on drawings;  manufacturer's white, elongated, open front seat, less cover, with stainless steel check hinges; or  ___>>​​.

Floor-Mounted, Back-Outlet, Flush Valve Water Closets​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​:

Basis of Design:  Zurn Water, LLC; Z5635-BWL, << 14-inch (356 mm)>>​ rim height.

Basis of Design:  Zurn Water, LLC; Z5645-BWL, << 16-5/8-inch (422 mm)>> ADA rim height.

Description:  <<ASME A112.19.2>>, vitreous china, siphon-jet flush. Provide bolt caps.

Provide with ZurnSHIELD glaze to inhibit growth of mold, mildew, and bacteria.

Bowl:  Elongated.

Spud:  Top spud, << 1-1/2 inches (38 mm)>>.

Color:  White.

Toilet Seat:  Provide ​​<< as indicated on drawings;  manufacturer's white, elongated, open front seat, less cover, with stainless steel check hinges; or  ___>>​​.

Child-Height Floor-Mounted, Bottom-Outlet, Flush Valve Water Closets​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​:

Basis of Design:  Zurn Water, LLC; Z5675-BWL.

Description:  Child-height, <<ASME A112.19.2>>, vitreous china, siphon-jet flush. Provide bolt caps.

Bowl:  Elongated.

Spud:  Top spud, << 1-1/2 inches (38 mm)>>.

Color:  White.

Toilet Seat:  Provide ​​<< as indicated on drawings;  manufacturer's white, juvenile, open front seat, less cover, with stainless steel check hinges; or  ___>>​​.

Urinals

Wall-Hung, Siphon-Jet Urinals<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>:

Basis of Design:  Zurn Water, LLC; Z5730.

Description:  <<ASME A112.19.2>>, vitreous china with vandal-resistant outlet strainer.

Spud:  Top spud, << 3/4 inch (19 mm)>>.

Color:  White.

Wall-Hung, Washout Urinals​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​:

Basis of Design:  Zurn Water, LLC; Z5755-U, top spud.

Basis of Design:  Zurn Water, LLC; Z5765-U, rear spud.

Description:  <<ASME A112.19.2>>, vitreous china with vandal-resistant outlet strainer.

Urinal Backwall:  Proprietary asymmetric design.

Spud Location:  ​​<< Top spud;  Rear spud; or  ______>>​​.

Spud Size:  << 3/4 inch (19 mm)>>.

Color:  White.

Wall-Hung, Ultra-Low Consumption, Pint, Washout Urinals<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>:

Basis of Design:  Zurn Water, LLC; Z5738-U, top spud.

Basis of Design:  Zurn Water, LLC; Z5755-U, top spud.

Basis of Design:  Zurn Water, LLC; Z5765-U, rear spud.

Description:  <<ASME A112.19.2>>, vitreous china, designed to flush with ​<< 0.125 gal (0.5 L)>>​ per flush; vandal-resistant outlet strainer.

Urinal Backwall:  Proprietary asymmetric design.

Spud Location:  ​​​<< Top spud;  Rear spud; or  ______>>​​​.

Spud Size:  ​<< 3/4 inch (19 mm)>>​.

Color:  White.

Wall-Hung, Waterless Urinals<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>:

Basis of Design:  Zurn Water, LLC; Z5795.

Description:  <<ASME A112.19.2>>, vitreous china, with strainer, integral trap, and back outlet.

Color:  White.

Accessories:  Provide manufacturer's trap-sealing liquid.

Flush Valves - Water Closet

Exposed Hydropowered, Gear-Driven Sensor Flush Valves<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>:

Basis of Design:  Zurn Water, LLC; ZER6000AV-HYD.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; chrome-plated brass body, gear-driven ceramic cartridge, diaphragm flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and tailpiece.

Override:  True mechanical type; allows flushing when power is not available.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Power:  Water-driven, turbine-powered battery with backup alkaline batteries.

Flush Volume:  ​<< 1.1 gal (4.1 L);  1.28 gal (4.8 L);  1.6 gal (6.0 L); or  ____ gal (____ L)>>​ per flush.

Dual Flush Volume:  ​​<< 1.28 / 1.1 gal (4.8 / 4.1 L);  1.6 / 1.1 gal (6.0  / 4.1 L); or  ____ / ____ gal (____ / ____ L)>>​​ per flush.

Fixture Connection:  << 1-1/2-inch (38 mm)>> top spud.

Features:

Hygiene flush.

User-in-view LED light.

Backup battery status light.

plumbPro:  Provide fixture with electronics module for wireless connectivity to Zurn's plumbPro mobile application.

plumbSMART:  Provide fixture with electronics module for wireless connectivity to Zurn's plumbSMART fixture-monitoring software.

Alternate Finish:  ​<< Brushed nickel;  Matte black; or  ___>>​.

Exposed Gear-Driven Flush Valves with Top-Mounted Sensors<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>:

Basis of Design:  Zurn Water, LLC; ZER-TM Series, battery powered.

Basis of Design:  Zurn Water, LLC; ZER-TM-HW Series, hardwired.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; chrome-plated brass body, gear-driven ceramic cartridge, diaphragm flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Override:  True mechanical type; allows flushing when power is not available.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Power:  ​​​​​<< Battery powered;  Hardwired with battery backup; or  ___>>​​​​​.

Flush Volume:  ​<< 1.1 gal (4.1 L);  1.28 gal (4.8 L);  1.6 gal (6.0 L); or  ____ gal (____ L)>>​ per flush.

Dual Flush Volume:  ​​​<< 1.6 / 1.1 gal (6.0 / 4.1 L); or  ____ / ____ gal (____ / ____ L)>>​​​ per flush.

Fixture Connection:  << 1-1/2-inch (38 mm)>> top spud.

Features:

Hygiene flush.

User-in-view LED light.

Battery status light.

Exposed Gear-Driven Flush Valves with Side-Mounted Sensors​​​​​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​​​​​:

Basis of Design:  Zurn Water, LLC; ZER-CPM Series, battery powered.

Basis of Design:  Zurn Water, LLC; ZER-SM Series, battery powered.

Basis of Design:  Zurn Water, LLC; ZEMS-IS Series, hardwired.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​​; chrome-plated brass body, gear-driven ceramic cartridge, diaphragm flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Power:  ​​​​​​​​<< Battery powered;  Hardwired; or  ___>>​​​​​​​​.

Flush Volume:  ​<< 1.1 gal (4.1 L);  1.28 gal (4.8 L);  1.6 gal (6.0 L);  3.5 gal (13.2 L); or  ____ gal (____ L)>>​ per flush.

Fixture Connection:  << 1-1/2-inch (38 mm)>> top spud.

Features, Battery Powered:

Hygiene flush.

User-in-view LED light.

Battery status light.

Features, Hardwired:

Hygiene flush.

User-in-view LED light.

plumbSMART:  Provide fixture with electronics module for wireless connectivity to Zurn's plumbSMART fixture-monitoring software.

Exposed Gear-Driven Flush Valves with Concealed Sensors​​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​​:

Basis of Design:  Zurn Water, LLC; ZEMS Series.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>; chrome-plated brass body, gear-driven ceramic cartridge, diaphragm flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Power:  Hardwired.

Flush Volume:  ​<< 1.1 gal (4.1 L);  1.28 gal (4.8 L);  1.6 gal (6.0 L);  3.5 gal (13.2 L); or  ____ gal (____ L)>>​ per flush.

Fixture Connection:  << 1-1/2-inch (38 mm)>> top spud.

Features:

Hygiene flush.

User-in-view LED light.

plumbSMART:  Provide fixture with electronics module for wireless connectivity to Zurn's plumbSMART fixture-monitoring software.

Concealed Gear-Driven Flush Valves​​​​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​​​​:

Basis of Design:  Zurn Water, LLC; ZEMS Series.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; brass body, gear-driven ceramic cartridge, diaphragm flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Power:  Hardwired.

Flush Volume:  ​<< 1.1 gal (4.1 L);  1.28 gal (4.8 L);  1.6 gal (6.0 L);  3.5 gal (13.2 L); or  ____ gal (____ L)>>​ per flush.

Fixture Connection:  << 1-1/2-inch (38 mm)>> << top;  rear; or  ______>> spud.

Features:

Hygiene flush.

User-in-view LED light.

Accessories:  Full-size stainless steel valve cover with vandal-resistant screws.

Exposed Piston Flush Valves with Top-Mounted Sensors​​​​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​​​​:

Basis of Design:  Zurn Water, LLC; ZTR Series.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; chrome-plated brass body, solenoid-operated piston flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Power:  Battery powered.

Flush Volume:  ​​<< 1.1 gal (4.1 L);  1.28 gal (4.8 L);  1.6 gal (6.0 L); or  ____ gal (____ L)>>​​ per flush.

Dual Flush Volume:  ​​​<< 1.6 / 1.1 gal (6.0 / 4.1 L); or  ____ / ____ gal (____ / ____ L)>>​​​ per flush.

Fixture Connection:  << 1-1/2-inch (38 mm)>> top spud.

Features:

Hygiene flush.

User-in-view LED light.

Battery status light.

plumbSMART:  Provide fixture with electronics module for wireless connectivity to Zurn's plumbSMART fixture-monitoring software.

Manual Flush Valves​​​​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​​​​:

Basis of Design:  Zurn Water, LLC; AV Series.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; exposed, chrome-plated brass body, diaphragm flush valve; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Flush Volume:  ​<< 1.1 gal (4.1 L);  1.28 gal (4.8 L);  1.6 gal (6.0 L);  3.5 gal (13.2 L); or  ____ gal (____ L)>>​ per flush.

Dual Flush Volume:  ​​<< 1.6 / 1.1 gal (6.0 / 4.1 L);  3.5 / 2.4 gal (13.2 / 9.1 L); or  ____ / ____ gal (____ / ____ L)>>​​ per flush.

Fixture Connection:  << 1-1/2-inch (38 mm)>> top spud.

Flush Valves - Urinal

Exposed, Hydropowered, Gear-Driven Flush Valves​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​:

Basis of Design:  Zurn Water, LLC; ZER6003AV-HYD.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; chrome-plated brass body, gear-driven ceramic cartridge, diaphragm flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and tailpiece.

Override:  True mechanical type; allows flushing when power is not available.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Power:  Water-driven, turbine-powered battery with backup alkaline batteries.

Flush Volume:  ​<< 0.125 gal (0.5 L);  0.5 gal (1.9 L);  1.0 gal (3.8 L); or  ____ gal (____ L)>>​ per flush.

Fixture Connection:  << 3/4-inch (19 mm)>> top spud.

Features:

Hygiene flush.

User-in-view LED light.

Backup battery status light.

Alternate Finish:  << Brushed nickel;  Matte black; or  ______>>.

plumbPro:  Provide fixture with electronics module for wireless connectivity to Zurn's plumbPro mobile application.

plumbSMART:  Provide fixture with electronics module for wireless connectivity to Zurn's plumbSMART fixture-monitoring software.

Exposed Gear-Driven Flush Valves with Top-Mounted Sensors​​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​​:

Basis of Design:  Zurn Water, LLC; ZER-TM Series, battery powered.

Basis of Design:  Zurn Water, LLC; ZER-TM-HW Series, hardwired.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; chrome-plated brass body, gear-driven ceramic cartridge, diaphragm flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Override:  True mechanical type; allows flushing when power is not available.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Power:  ​​​​​<< Battery powered;  Hardwired with battery backup; or  ___>>​​​​​.

Flush Volume:  ​<< 0.125 gal (0.5 L);  0.5 gal (1.9 L);  1.0 gal (3.8 L); or  ____ gal (____ L)>>​ per flush.

Fixture Connection:  << 3/4-inch (19 mm)>> top spud.

Features:

Hygiene flush.

User-in-view LED light.

Battery status light.

Exposed Gear-Driven Flush Valves with Side-Mounted Sensors​​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​​:

Basis of Design:  Zurn Water, LLC; ZER-CPM Series, battery powered.

Basis of Design:  Zurn Water, LLC; ZER-SM Series, battery powered.

Basis of Design:  Zurn Water, LLC; ZEMS-IS Series, hardwired.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; chrome-plated brass body, gear-driven ceramic cartridge, diaphragm flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Power:  ​​​​​​<< Battery powered;  Hardwired; or  ___>>​​​​​​.

Flush Volume:  ​<< 0.125 gal (0.5 L);  0.5 gal (1.9 L);  1.0 gal (3.8 L);  1.5 gal (5.7 L); or  ____ gal (____ L)>>​ per flush.

Fixture Connection:  << 3/4-inch (19 mm)>> top spud.

Features, Battery Powered:

Hygiene flush.

User-in-view LED light.

Battery status light.

Features, Hardwired:

Hygiene flush.

User-in-view LED light.

plumbSMART:  Provide fixture with electronics module for wireless connectivity to Zurn's plumbSMART fixture-monitoring software.

Exposed Gear-Driven Flush Valves with Concealed Sensors​​​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​​​:

Basis of Design:  Zurn Water, LLC; ZEMS Series.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; chrome-plated brass body, gear-driven ceramic cartridge, diaphragm flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Power:  Hardwired.

Flush Volume:  ​<< 0.125 gal (0.5 L);  0.5 gal (1.9 L);  1.0 gal (3.8 L);  1.5 gal (5.7 L); or  ____ gal (____ L)>>​ per flush.

Fixture Connection:  << 3/4-inch (19 mm)>> top spud.

Features:

Hygiene flush.

User-in-view LED light.

plumbSMART:  Provide fixture with electronics module for wireless connectivity to Zurn's plumbSMART fixture-monitoring software.

Concealed Gear-Driven Flush Valves​​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​​:

Basis of Design:  Zurn Water, LLC; ZEMS Series.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; brass body, gear-driven ceramic cartridge, diaphragm flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Power:  Hardwired.

Flush Volume:  ​<< 0.125 gal (0.5 L);  0.5 gal (1.9 L);  1.0 gal (3.8 L);  1.5 gal (5.7 L); or  ____ gal (____ L)>>​ per flush.

Fixture Connection:  << 3/4-inch (19 mm)>> << top;  rear; or  ______>> spud.

Features:

Hygiene flush.

User-in-view LED light.

Accessories:  Full-size stainless steel valve cover with vandal-resistant screws.

Exposed Piston Flush Valves with Top-Mounted Sensors​​​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​​​:

Basis of Design:  Zurn Water, LLC; ZTR Series.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; chrome-plated brass body, solenoid-operated piston flush valve; sensor activation with override button; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Power:  Battery powered.

Flush Volume:  ​​<< 0.125 gal (0.5 L);  0.25 gal (0.9 L);  0.5 gal (1.9 L);  1.0 gal (3.8 L); or  ____ gal (____ L)>>​​ per flush.

Fixture Connection:  << 3/4-inch (19 mm)>> top spud.

Features:

Hygiene flush.

User-in-view LED light.

Battery status light.

plumbSMART:  Provide fixture with electronics module for wireless connectivity to Zurn's plumbSMART fixture-monitoring software.

Manual Flush Valves​​​​<< , Plan Code ______;  , Plan Tag ______;  , Type ______; or  None - N/A>>​​​​:

Basis of Design:  Zurn Water, LLC; AV Series.

Description:  <<ASSE 1037/ASME A112.1037/CSA B125.37>>​; exposed, chrome-plated brass body, diaphragm flush valve; with integral vacuum breaker, stop valve, and adjustable tailpiece.

Diaphragm:  Triple-filtered bypass design; chemical-resistant thermoplastic elastomer.

Flush Volume:  ​<< 0.125 gal (0.5 L);  0.5 gal (1.9 L);  1.0 gal (3.8 L); or  ____ gal (____ L)>>​ per flush.

Fixture Connection:  << 3/4-inch (19 mm)>> top spud.

Fixture Carriers

Water Closet Carriers:

Basis of Design:  Zurn Water, LLC; Z1201-N Series.

Assembly:  <<ASME A112.6.1M>>; epoxy-coated cast-iron frame, no-hub waste and vent connections, adjustable faceplate with gaskets, and anchors for floor and wall attachment. Provide threaded bolts to secure fixture.

Urinal Carriers:

Basis of Design:  Zurn Water, LLC; Z1221, urinal carrier.

Basis of Design:  Zurn Water, LLC; Z1222, urinal carrier with additional lower bearing plate.

Assembly:  <<ASME A112.6.1M>>; in-wall, floor-mounted carrier in epoxy-coated steel with fixture hanger plate, structural uprights, and welded feet. Provide anchors to secure uprights to floor. Provide threaded bolts to secure urinal to plate.

Provide with lower bearing plate.

PART 3  EXECUTION

Examination

Verify walls, floors, and finishes are prepared and ready for installation of fixtures.

Verify rough-ins for field connections match sizes and locations indicated on drawings.

Installation

Install products in accordance with manufacturer's instructions.

Install wall-mounted fixtures at heights indicated on drawings.

Install fixtures level and plumb.

Install and secure fixtures in place.

Install fresh batteries in battery-powered fixtures at time of <<mm-dd-yyyy>>.

Field Quality Control

See Section ​<< 014000 - Quality Requirements>>​ for additional requirements.

Inspect each product for damage and defects.

Test fixtures after installation to verify operation.

Replace damaged or defective products.

Adjusting

Adjust fixture stops and valves to intended water flow rate. Confirm fixtures operate without splashing, noise, or overflow.

Adjust sensor range on sensor-operated fixtures.

Cleaning

See Section ​<< 017000 - Execution and Closeout Requirements>>​ for additional requirements.

Clean plumbing fixtures to remove dirt, fingerprints, paint, and other foreign material. Restore finishes to match original factory finish.

Protection

Protect installed products from damage due to subsequent construction operations.

Do not permit construction personnel to use fixtures.

- END OF SECTION